YB3-W、YB3-TH、YB3-THW、YB3-TA、YB3-TAW Series Flameproof Three Phase Asynchronous Motor

(Frame size 63 to 355)

Operating Instruction Manual

February,2015

Preface

My sincere customer:

Thank you for your buy and use "XIANDA" brand motor, our company will serve you wholeheartedly.

The quality policy of "elaborate design, strict management, continuous improvement, customer satisfaction" is the permanent pursuit of our company. We can provide products with good quality and low price, and we promised to provide satisfactory after-sales service through product installation, commissioning to the use process for you, thus to achieve our win-win cooperation.

Our company passed the national standard of GB/T 19001 - ISO9001 quality system certification ( (issued by Shanghai SAC) in 1999. And we also passed through the GB/T 19001 - ISO9001 standard quality system certification (China classification society) in 2002, 2008 and 2012.

The instruction manual can help the operators to understand the general characteristics of the motor, but the users can also apply personal experiences into the equipment installation, operation and maintenance work. If the general descriptions and graphs in the instruction show conflicts with the supplementary material, the latter one is the priority. The diagrams in this instruction manual describe the typical motor, and they are not applicable to special conditions.

Please read through this instruction manual before you install and use the product, and then install, debug and use the product as required.

This manual is a general technical guidance document, the parameters may be different and change with the advance of technology, but will not affect normal installation and use. Pls forgive if bring you any inconvenience.

YB3-W、YB3-TH、YB3-THW、YB3-TA、YB3-TAW

Serie Flameproof Three Phase Asynchronous Motor

- Scope

      - YB3-W、YB3-TH、YB3-THW、YB3-TA、YB3-TAW series flameproof three-phase asynchronous motor (hereinafter referred to as "motor") is a new generation of newly developed squirrel-cage three-phase asynchronous motor with high efficiency and energy saving. It is manufactured according to the specification of Q/320206JLAB83-2010《Flameproof Three Phase Asynchronous Motor– Part I: YB3-W、YB3-TH、YB3-THW、YB3-TA、YB3-TAW Series Flameproof Three Phase Asynchronous Motor（Frame size 63～355）》.This motor show beautiful appearance, high performance, reliable operation and simple maintenance.The efficiency index of this series motors confirms to the energy efficiency grades 3 of specified in GB18613-2012 Minimum allowable values of energy efficiency and the energy efficiency grades for small and medium three-phase asynchronous motors.

      - The motors of this serial model  possess the explosion-proof performance satisfying the specifications of GB3836.1-2010《Explosive atmosphere – Part I: Equipment- General requirements》and GB3836.2-2010《Explosive atmosphere – Part II: Equipment protection by flameproof enclosure“d”》.  The motors whose explosive markings is ExdIIAT1～T4 Gb、ExdIIBT1～T4 Gb can be applied to the affixed equipment in explosive gas areas-zone 1 and zone 2, where the grade is IIA or IIB and temperature group T1 to T4. General explosive gas are shown in table 1.

Table 1.

| Class | Temperature group |  |  |  |
| --- | --- | --- | --- | --- |
|  | T1 | T2 | T3 | T4 |
| IIA | Methane, Ethane, Propane, Styrene, Benzene, Toluene, Xylol, Carbon monoxide, Acetic acid. Ammonia | Byjtane, Propane, Ethyl benzene, Methanol, Alcohol, Propanel, Butanol | Pentane, Hezane, Heptane, Octane, Decane, Cyclohexane, Diesel-oil, Motor petrol. |  |
| IIB | Propine, Cycloproqane, Coking gas. | Ethylene, Oxirane, 1,3-butadiene, 1.2-epoxy propane. | Dimethyl-ether, Four-hydro, Furfuryl alcohol, Butenal, Propenal, Hydrosulfide. | Ethyl-methyl ether, Ether, Four-fluoro Ethylene. |

      - Definition of the explosion-proof mark:

Ex   d   IIB   T4   Gb

Explosive markings                                         Equipment for protection

level（EPL）Gb

The flameproof enclosure                                     Temperature class of an

Group of an electrical apparatus                               electrical apparatus

Significance of （EPL）Gb: equipment for explosive gas atmosphere, with “high” protection level, not the ignition source under the condition of normal operation or expected failures. Protection concept of most standards puts forward that equipment is at this level.

Significance of （EPL）Mb: equipment installed in the environment with methane explosion in coal mine, with “high” protection level. This level has enough security, making it impossible for the equipment to become ignition source during normal operation or under the condition of expected failures occurring in the time period from gas outburst to equipment power-off.

4.  Definition of the motor model:

Y  B     3 - 160   M  1  - 4 - W

Induction motor                                            Environment code

Flameproof type                                           Number of poles

The third remodeling design                                 Length code of iron core

Center height of motor                             Frame length (S-Short, M-Medium, L-Long)

Note 1: TH-- Moist and tropic THW-- Moist and tropic in outdoors

TA—Dry and tropic TAW-- Dry and tropic in outdoors

The mechanism of flameproof motor: the shell can withstand internal explosion of combustible mixture which can infiltrate into the inside of the shell from any shell joint face or structure clearance, and will not caused explosive gas lighting by a variety of gas or vapor in outside.

- Operating conditions of the motor:

        - The maximum ambient temperature is 40ºC(for W,TH and THW)；45ºC（for TA）；55ºC(for TAW); The minimum ambient temperature is -20ºC(for W); -10ºC(for THW and TAW)；-5ºC(for TH and TA);Refer to the specifications of GB755 when the motors are used with over 1000m absolute elevation or under the ambient temperature lower than 40ºC;

        - The relative humidity of ambient atmosphere should not exceed 100%(for W);95%（for TH,THW,TA and TAW）（with the temperature of 28ºC）;

        - The operational absolute elevation should not exceed 1000m; (If the motor works at an altitude of more than 1000m, the temperature rise of the motor should be corrected according to the national standard GB 755 "rotary motor quota and performance ")

        - Voltages：380V,660V,380/660V;(or range scope of 200 to 690V)

        - Frequency：50HZ;

        - Operation mode：S1（Continuous）;

        - Connection method：Y(3kw or the below),△/Y(3kw the above);

- The nominal power series of the motor are:

0.12、0.18、0.25、0.37、1.1、1.5、2.2、3、4、5.5、7.5、11、15、18.5、22、30、37、45、55、75、90、110、132、160、（185）、200、（220）、250、（280）、315、（355）kW。

Note: The bracketed ones are non-recommended models.

- Pls refer to table 2 of the relationship between the motor seat No, the motor power and rotate speed.

Table 2

| Frame size | Synchro-speed （r/min） |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 3000 | 1500 | 1000 | 750 | 600 | 500 | 429 | 375 |
|  | Power kW |  |  |  |  |  |  |  |
| 63M1 | 0.18 | 0.12 | － | － | － | － | － | － |
| 63M2 | 0.25 | 0.18 |  |  |  |  |  |  |
| 71M1 | 0.37 | 0.25 | 0.18 |  |  |  |  |  |
| 71M2 | 0.55 | 0.37 | 0.25 |  |  |  |  |  |
| 80M1 | 0.75 | 0.55 | 0.37 | 0.18 |  |  |  |  |
| 80M2 | 1.1 | 0.75 | 0.55 | 0.25 |  |  |  |  |
| 90S | 1.5 | 1.1 | 0.75 | 0.37 |  |  |  |  |
| 90L | 2.2 | 1.5 | 1.1 | 0.55 |  |  |  |  |
| 100L1 | 3 | 2.2 | 1.5 | 0.75 |  |  |  |  |
| 100L2 |  | 3 |  | 1.1 |  |  |  |  |
| 112M | 4 | 4 | 2.2 | 1.5 |  |  |  |  |
| 132S1 | 5.5 | 5.5 | 3 | 2.2 |  |  |  |  |
| 132S2 | 7.5 |  |  |  |  |  |  |  |
| 132M1 | － | 7.5 | 4 | 3 |  |  |  |  |
| 132M2 |  |  | 5.5 |  |  |  |  |  |
| 160M1 | 11 | 11 | 7.5 | 4 |  |  |  |  |
| 160M2 | 15 |  |  | 5.5 |  |  |  |  |
| 160L | 18.5 | 15 | 11 | 7.5 |  |  |  |  |
| 180M | 22 | 18.5 | － | － |  |  |  |  |
| 180L | － | 22 | 15 | 11 |  |  |  |  |
| 200L1 | 30 | 30 | 18.5 | 15 |  |  |  |  |
| 200L2 | 37 |  | 22 |  |  |  |  |  |
| 225S | － | 37 | － | 18.5 |  |  |  |  |
| 225M | 45 | 45 | 30 | 22 |  |  |  |  |
| 250M | 55 | 55 | 37 | 30 |  |  |  |  |
| 280S | 75 | 75 | 45 | 37 |  |  |  |  |
| 280M | 90 | 90 | 55 | 45 |  |  |  |  |
| 315S | 110 | 110 | 75 | 55 | 45 | 37 |  |  |
| 315M | 132 | 132 | 90 | 75 | 55 | 45 | 37 | 30 |
| 315L1 | 160 | 160 | 110 | 90 | 75 | 55 | 45 | 37 |
| 315L2 | 200 | 200 | 132 | 110 | 90 | 75 | 55 | 45 |
| 355S1 | （185） | （185） | 160 | 132 | （90） | 75 | 55 | 55 |
| 355S2 | （200） | （200） |  |  |  |  | 75 | 75 |
| 355M1 | （220） | （220） | （185） | 160 | 110 | 90 | 90 | 90 |
| 355M2 | 250 | 250 | 200 |  | 132 | 110 |  |  |
| 355L1 | （280） | （280） | （220） | （185） | 160 | 132 | 110 | － |
| 355L2 | 315 | 315 | 250 | 200 | （185） |  | 132 |  |
| 355L3 | （355） | （355） | （280） | （220） | 200 | － | － |  |
| Note 1: The bracketed ones are non-recommended models. Note 2：Number 1,2,3 behind S,M,L represent respectively different power for identical frame size and rotate speed. |  |  |  |  |  |  |  |  |

- Structural features

  - Refer to Fig. 1 for the details of motor structure.

  - The protective class of the motor housing is IP55. (Protection grade is composed of the letters "IP" and two numbers attached to the back)

1) The first number characterize the protection class of the shell enclosure to people or items, "5" show that the motor shell can prevent touching or approaching to the shell charged or rotating parts. Though the shell can not completely be dust-proof, the small dust quantity is not enough to affect the normal operation of the machine.

2) The second number represent protection grade of the harmful effects caused by the water. "5" said hydraulic motor, carry water in any direction should have no harmful effects.

  - The cooling method of the motor is IC 411. (It is surface cooling for the motor base. The motor are enclosed and show no inside and outside air exchange function. The internal cooling air only cycled inside the motor through the fan driver. The cooling air takes away heat when it flows through the stator iron core or other heating components such as coil, and then passed through a variety of heat conduction ways to the motor base. Finally transfer heat to the outside envirment by the rear cabin fan blowing the base surface, thus to achieve the cooling effect.)

  - The frames of the motors are fabricated by welding steel plates, and other components are made of gray cast-iron with grades above HT 250.

  - Mounting arrangements, manufacturing specifications (frame sizes) and constructions are shown in the table 3.

Table 3

  - The motor connection box locates on the upper of motor with six wiring terminals (or three wiring terminals when the rated output of motor is under 3kw) and one ground terminal in it. It adopts horn-type or thread-type wire outlets, referring to connection box structural scheme for details (Fig.2). Give a remark on the ordering sheet when the customer selects thread-type wire outlets.

  - Wire inlets are equipped with seal rings (Refer to Fig. 3), which have several concentric circles. When application, select proper inner diameter of the seal ring according to the outer diameter of the cable ensuring that there is no gap between the seal ring and the cable, and between the seal ring and the connection box after the cover of the connection box is pressed tightly. Otherwise it will not function as explosion-proof.

  - The insulating grade of the motor is F. The temperature rise of stator windings has the upper limit of 80K when measured with resistance method (The 2nd and 4th poles with 315L frame size, and the motor with 355 frame size subject to the upper temperature rise limit of 105K). The temperature rise limit of motors should be altered according to the specifications of GB 755 when the absolute elevation and ambient temperature deviate from the specifications in clause 5.

  - All the components of the explosion-proof motor housing should pass the static pressure tests. The frames, end covers, axles, bearing inner caps, connection box seats and the box covers, terminal sockets, seal rings all belongs to the explosion-proof components. The binding bolts for connecting explosion-proof components are equipped with spring gaskets to avoid getting loose.

  - The motor housing is equipped with grounding bolts and labeled with grounding denotes.

- Principal technical parameters

1. The vibration intensity limit (root-mean-square value) for no-load motor should comply with the provisions in table 4.

Table 4

|  | 63≤H≤132 |  |  | 132﹤H≤280 |  |  | H＞280 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Way of installation | Displacement (µm) | Speed (mm/s) | Acceleration (m/s2) | Displacement (µm) | Speed (mm/s) | Acceleration (m/s2) | Displacement (µm) | Speed (mm/s) | Acceleration (m/s2) |
| Free suspension | 25 | 1.6 | 2.5 | 35 | 2.2 | 3.5 | 45 | 2.8 | 4.4 |
| Rigidity installation | 21 | 1.3 | height of center for shaft （mm） | 29 | 1.8 | 2.8 | 37 | 2.3 | 3.6 |
| Note 1： The specified limit in the table are all A level parameters.. Note 2： The interface frequency of displacement and velocity, velocity and acceleration are 10 hz and 250 hz, respectively. |  |  |  |  |  |  |  |  |  |

2. When the motor power, voltage and frequency are rated, its guarantee value of efficiency (Accord with 3 grade of GB 18613-2012 energy efficiency level) shall comply with the provisions of the table 5. Efficiency value is determined by input - output power loss analysis (refer to GB/T1032). In calculation, the efficiency value are four significant digits, power factor value take three significant digits. Shaft sealing ring should be unload when doing the measurement.

Table 5

| Power kW | Synchro-speed （r/min） |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 3000 | 1500 | 1000 | 750 | 600 | 500 | 429 | 375 | 3000 | 1500 | 1000 | 750 | 600 | 500 | 429 | 375 |
|  | Efficiency η％ |  |  |  |  |  |  |  | Power factor COSφ |  |  |  |  |  |  |  |
| 0.12 | — | 58.0 | — | — | — | — | — | — | — | 0.72 | — | — | — | — | — | — |
| 0.18 | 66.0 | 63.0 | 62.0 | 52.0 |  |  |  |  | 0.80 | 0.73 | 0.66 | 0.61 |  |  |  |  |
| 0.25 | 68.0 | 66.0 | 63.0 | 55.0 |  |  |  |  | 0.81 | 0.74 | 0.68 |  |  |  |  |  |
| 0.37 | 70.0 | 69.0 |  | 63.0 |  |  |  |  |  | 0.75 | 0.70 | 0.62 |  |  |  |  |
| 0.55 | 73.0 | 80.7 | 75.4 | 64.0 |  |  |  |  | 0.83 | 0.76 | 0.72 | 0.63 |  |  |  |  |
| 0.75 | 77.4 | 79.6 | 75.9 | 71.0 |  |  |  |  | 0.82 | 0.76 | 0.71 | 0.68 |  |  |  |  |
| 1.1 | 79.6 | 81.4 | 78.1 | 73.0 |  |  |  |  | 0.83 | 0.77 | 0.72 | 0.69 |  |  |  |  |
| 1.5 | 81.3 | 82.8 | 79.8 | 75.0 |  |  |  |  | 0.84 | 0.78 | 0.72 |  |  |  |  |  |
| 2.2 | 83.2 | 84.3 | 81.8 | 79.0 |  |  |  |  | 0.85 | 0.80 | 0.72 | 0.73 |  |  |  |  |
| 3 | 84.6 | 85.5 | 83.3 | 81.0 |  |  |  |  | 0.87 | 0.81 | 0.72 |  |  |  |  |  |
| 4 | 85.8 | 86.6 | 84.6 |  |  |  |  |  | 0.88 | 0.81 | 0.74 |  |  |  |  |  |
| 5.5 | 87.0 | 87.7 | 86.0 | 83.0 |  |  |  |  | 0.88 | 0.82 | 0.75 | 0.75 |  |  |  |  |
| 7.5 | 88.1 | 88.7 | 87.2 | 88.5 |  |  |  |  | 0.89 | 0.83 | 0.78 | 0.76 |  |  |  |  |
| 11 | 89.4 | 89.8 | 88.7 | 87.0 |  |  |  |  | 0.89 | 0.83 | 0.79 |  |  |  |  |  |
| 15 | 90.3 | 90.6 | 89.7 | 89.0 |  |  |  |  | 0.89 | 0.84 | 0.81 |  |  |  |  |  |
| 18.5 | 90.9 | 91.2 | 90.4 | 90.0 |  |  |  |  | 0.89 | 0.86 | 0.80 | 0.78 |  |  |  |  |
| 22 | 91.3 | 91.6 | 90.9 | 90.5 |  |  |  |  | 0.89 | 0.86 | 0.81 |  |  |  |  |  |
| 30 | 92.0 | 92.3 | 91.7 | 91.0 |  |  |  | 90.5 | 0.89 | 0.85 | 0.82 | 0.79 |  |  |  | 0.66 |
| 37 | 92.5 | 92.7 | 92.2 | 91.5 |  | 91.5 | 91.0 |  | 0.89 | 0.86 | 0.83 |  |  | 0.72 | 0.70 |  |
| 45 | 92.9 | 93.1 | 92.7 | 92.0 | 91.5 |  |  |  | 0.89 | 0.86 | 0.85 |  | 0.75 |  |  |  |
| 55 | 93.2 | 93.5 | 93.1 | 92.8 | 92.0 |  | 92.0 | 90.8 | 0.89 | 0.86 | 0.86 | 0.81 |  |  |  | 0.68 |
| 75 | 93.8 | 94.0 | 93.7 | 93.5 | 92.5 |  |  |  | 0.89 | 0.87 | 0.84 |  | 0.76 |  | 0.72 |  |
| 90 | 94.1 | 94.2 | 94.0 | 93.8 | 93.0 | 93.0 | 92.5 |  | 0.89 | 0.88 | 0.85 | 0.82 | 0.77 | 0.73 |  |  |
| 110 | 94.3 | 94.5 | 94.3 | 94.0 | 93.2 | 93.5 | 92.5 | — | 0.90 | 0.89 | 0.85 |  | 0.78 | 0.75 |  | — |
| 132 | 94.6 | 94.7 | 94.6 | 94.2 | 93.5 |  | 93.6 |  | 0.90 | 0.89 | 0.86 |  |  |  | 0.77 |  |
| 160 | 94.8 | 94.9 | 94.8 |  |  | — | — |  | 0.91 | 0.90 | 0.87 |  |  | — | — |  |
| (185) | 94.9 | 95.0 | 94.9 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 200 | 95.0 | 95.1 | 95.0 | 94.5 | 93.6 |  |  |  |  |  |  | 0.83 | 0.79 |  |  |  |
| (220) |  |  |  | 93.7 | — |  |  |  |  |  |  | 0.82 | — |  |  |  |
| 250 |  |  |  | — |  |  |  |  |  |  |  | — |  |  |  |  |
| (280) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 315 |  |  | — |  |  |  |  |  |  |  | — |  |  |  |  |  |
| 355 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

3. Under the nominal voltage the ratio of motor lock torque and its nominal torque, and the ratio of motor lock current and its nominal current should not be lower than the specifications listed in table 6.

Table 6

| Power kW | Synchro-speed（r/min） |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 3000 | 1500 | 1000 | 750 | 600 | 500 |  | 429 | 375 |  |
|  | Lock torque / nominal torque |  |  |  |  |  |  |  |  |  |
| 0.12 | — | 1.9 | 1.9 | 1.8 | — | — | — |  |  | — |
| 0.18 | 2.2 |  |  |  |  |  |  |  |  |  |
| 0.25 |  |  |  |  |  |  |  |  |  |  |
| 0.37 |  |  |  |  |  |  |  |  |  |  |
| 0.55 |  |  |  |  |  |  |  |  |  |  |
| 0.75 | 2.3 | 2.3 | 2.0 |  |  |  |  |  |  |  |
| 1.1 |  |  |  |  |  |  |  |  |  |  |
| 1.5 |  |  |  |  |  |  |  |  |  |  |
| 2.2 |  |  |  |  |  |  |  |  |  |  |
| 3 | 2.2 |  |  |  |  |  |  |  |  |  |
| 4 |  |  |  | 1.9 |  |  |  |  |  |  |
| 5.5 |  | 2.0 |  |  |  |  |  |  |  |  |
| 7.5 |  |  |  |  |  |  |  |  |  |  |
| 11 |  |  |  |  |  |  |  |  |  |  |
| 15 |  |  |  | 2.0 |  |  |  |  |  |  |
| 18.5 |  |  |  |  |  |  |  |  |  |  |
| 22 |  | 2.1 |  |  |  |  |  |  |  |  |
| 30 | 2.0 |  |  | 1.9 |  |  |  |  |  | 1.2 |
| 37 |  |  |  | 1.8 |  | 1.2 | 1.2 |  |  |  |
| 45 | 2.2 | 2.2 |  |  | 1.5 |  |  |  |  |  |
| 55 |  |  |  |  |  |  |  |  |  |  |
| 75 | 1.8 |  |  |  |  |  |  |  |  |  |
| 90 |  |  |  |  |  |  |  |  |  |  |
| 110 |  | 2.1 |  |  | 1.3 |  |  |  |  | — |
| 132 |  |  |  |  | 1.3 |  | 1.4 |  |  |  |
| 160 |  |  |  |  |  | — | — |  |  |  |
| （185） |  |  |  |  |  |  |  |  |  |  |
| 200 |  |  |  |  | 1.3 |  |  |  |  |  |
| （220） | 1.6 | 2.0 |  |  | — |  |  |  |  |  |
| 250 |  |  |  | — |  |  |  |  |  |  |
| （280） |  |  |  |  |  |  |  |  |  |  |
| 315 |  |  | — |  |  |  |  |  |  |  |
| 355 |  | 1.7 |  |  |  |  |  |  |  |  |

4. When the motor starts under the nominal voltage the ratio of minimum torque and the nominal torque, and the ratio of maximum torque and the nominal torque should not be lower than the specifications listed in table 7.

Table 7

| Power KW | Synchro-speed r/min |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 3000 | 1500 |  | 1000 | 750 | 600 | 500 | 429 | 375 |
|  | Minimum torque / nominal torque |  |  |  |  |  |  |  |  |
| 0.12 | — |  | 1.7 | — | — | — | — | — | — |
| 0.18 | 1.6 |  |  | 1.5 | 1.3 |  |  |  |  |
| 0.25 |  |  |  |  |  |  |  |  |  |
| 0.37 |  |  |  |  |  |  |  |  |  |
| 0.55 |  |  |  |  |  |  |  |  |  |
| 0.75 | 1.5 |  | 1.6 |  |  |  |  |  |  |
| 1.1 |  |  |  | 1.3 | 1.2 |  |  |  |  |
| 1.5 |  |  |  |  |  |  |  |  |  |
| 2.2 | 1.4 |  | 1.5 |  |  |  |  |  |  |
| 3 |  |  |  |  |  |  |  |  |  |
| 4 |  |  |  |  |  |  |  |  |  |
| 5.5 | 1.2 |  | 1.4 |  |  |  |  |  |  |
| 7.5 |  |  |  |  |  |  |  |  |  |
| 11 |  |  |  | 1.2 | 1.1 |  |  |  |  |
| 15 |  |  |  |  |  |  |  |  |  |
| 18.5 | 1.1 |  | 1.2 |  |  |  |  |  |  |
| 22 |  |  |  |  |  |  |  |  |  |
| 30 |  |  |  |  |  |  |  |  | 0.65 |
| 37 |  |  |  |  |  |  | 0.8 | 0.65 |  |
| 45 | 1.0 |  | 1.1 | 1.1 | 1.0 | 0.8 |  |  |  |
| 55 |  |  |  |  |  |  |  |  |  |
| 75 | 0.9 |  | 1.0 | 1.0 | 0.9 |  |  |  |  |
| 90 |  |  |  |  |  |  |  |  |  |
| 110 |  |  |  |  |  |  |  |  | — |
| 132 |  |  |  |  |  |  |  |  |  |
| 160 |  |  |  |  |  |  | — | — |  |
| （185） |  |  |  |  |  |  |  |  |  |
| 200 | 0.8 |  | 0.9 | 0.9 |  |  |  |  |  |
| （220） |  |  |  |  |  | — |  |  |  |
| 250 |  |  |  |  | — |  |  |  |  |
| （280） |  |  |  |  |  |  |  |  |  |
| 315 |  |  | 0.8 | — |  |  |  |  |  |
| 355 | 0.7 |  |  |  |  |  |  |  |  |

- When the motor starts under the nominal voltage the ratio of maximum torque and the nominal torque should not be lower than the specifications listed in table 8.

Table 8

| Power KW | Synchro-speed r/min |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 3000 | 1500 |  | 1000 |  | 750 | 600 | 500 | 429 | 375 |
|  | Maximum torque / nominal torque |  |  |  |  |  |  |  |  |  |
| 0.12 | — |  | 2.2 | — | — |  | — | — | — | — |
| 0.18 | 2.3 |  |  | 2.1 | 1.9 |  |  |  |  |  |
| 0.25 |  |  |  |  |  |  |  |  |  |  |
| 0.37 |  |  |  |  | 2.0 |  |  |  |  |  |
| 0.55 |  |  | 2.3 |  |  |  |  |  |  |  |
| 0.75 |  |  |  |  |  |  |  |  |  |  |
| 1.1 |  |  |  |  |  |  |  |  |  |  |
| 1.5 |  |  |  |  |  |  |  |  |  |  |
| 2.2 |  |  |  |  | 2.2 |  |  |  |  |  |
| 3 |  |  |  |  |  |  |  |  |  |  |
| 4 |  |  |  |  |  |  |  |  |  |  |
| 5.5 |  |  |  |  |  |  |  |  |  |  |
| 7.5 |  |  |  |  |  |  |  |  |  |  |
| 11 |  |  |  |  |  |  |  |  |  |  |
| 15 |  |  |  |  |  |  |  |  |  |  |
| 18.5 |  |  |  |  |  |  |  |  |  |  |
| 22 |  |  |  |  |  |  |  |  |  |  |
| 30 |  |  |  |  | 2.0 |  |  |  |  | 2.0 |
| 37 |  |  |  |  |  |  |  | 2.0 | 2.0 |  |
| 45 |  |  |  | 2.0 |  |  | 2.0 |  |  |  |
| 55 |  |  |  |  |  |  |  |  |  |  |
| 75 |  |  |  |  |  |  |  |  |  |  |
| 90 |  |  |  |  |  |  |  |  |  |  |
| 110 | 2.2 |  | 2.2 |  |  |  |  |  |  | — |
| 132 |  |  |  |  |  |  |  |  | 2.2 |  |
| 160 |  |  |  |  |  |  |  | — | — |  |
| （185） |  |  |  |  |  |  |  |  |  |  |
| 200 |  |  |  |  |  |  |  |  |  |  |
| （220） |  |  |  |  |  |  | — |  |  |  |
| 250 |  |  |  |  | — |  |  |  |  |  |
| （280） |  |  |  |  |  |  |  |  |  |  |
| 315 |  |  |  | — |  |  |  |  |  |  |
| 355 |  |  |  |  |  |  |  |  |  |  |

6. Under the rated voltage condition, the guarantee value of the ratio of the locked-rotor motor current and the rated current should not be greater than the provisions of the table 9. The rated current value can be aquired according to the rated power, rated voltage and the guarantee value of efficiency and power factor (excluding the tolerance).

Table 9

| Power KW | Synchro-speed r/min |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 3000 | 1500 | 1000 | 750 | 600 | 500 | 429 | 375 |
|  | Locked current / Nominal current |  |  |  |  |  |  |  |
| 0.12 | — | 4.0 | — | — | — | — | — | — |
| 0.18 | 5.0 |  | 4.0 | 3.3 |  |  |  |  |
| 0.25 |  |  |  |  |  |  |  |  |
| 0.37 | 5.5 |  |  | 4.0 |  |  |  |  |
| 0.55 |  | 6.3 |  |  |  |  |  |  |
| 0.75 | 6.8 | 6.4 | 5.8 |  |  |  |  |  |
| 1.1 | 7.1 | 6.6 | 5.9 |  |  |  |  |  |
| 1.5 | 7.3 | 6.7 |  |  |  |  |  |  |
| 2.2 | 7.6 | 7.3 | 6.2 | 5.5 |  |  |  |  |
| 3 | 7.8 | 7.5 | 6.4 |  |  |  |  |  |
| 4 | 8.1 |  | 6.6 | 6.0 |  |  |  |  |
| 5.5 | 8.2 |  | 6.8 |  |  |  |  |  |
| 7.5 | 7.8 | 7.3 |  |  |  |  |  |  |
| 11 | 7.9 | 7.4 | 6.9 |  |  |  |  |  |
| 15 |  | 7.5 | 7.3 | 6.5 |  |  |  |  |
| 18.5 | 8.0 | 7.6 | 7.2 |  |  |  |  |  |
| 22 | 8.1 | 7.7 | 7.3 |  |  |  |  |  |
| 30 | 7.5 | 7.1 | 6.8 |  |  |  |  | 5.0 |
| 37 |  | 7.3 | 7.0 | 6.0 |  | 5.0 | 5.0 |  |
| 45 |  |  | 7.2 |  | 6.0 |  |  |  |
| 55 | 7.6 |  |  | 6.5 |  |  |  |  |
| 75 | 6.9 | 6.8 | 6.5 |  |  |  |  |  |
| 90 | 9.6 | 6.9 | 6.6 |  |  |  |  |  |
| 110 | 7.0 |  |  |  | 5.5 |  |  | — |
| 132 |  |  |  |  |  |  | 4.4 |  |
| 160 | 7.1 |  | 6.7 |  |  | — | — |  |
| （185） |  |  |  |  |  |  |  |  |
| 200 |  |  | 6.8 |  |  |  |  |  |
| （220） |  |  |  |  | — |  |  |  |
| 250 |  |  |  | — |  |  |  |  |
| （280） |  |  |  |  |  |  |  |  |
| 315 | 7.2 |  | — |  |  |  |  |  |
| 355 | 7.2 | 6.5 |  |  |  |  |  |  |

7. The A weighted sound power level measured when the motor is in free-load state should have a sound level lower than the specifications in table 10. When the motor was loaded, the measured A sound power level shall be in accordance with the sum of specific value in table 10 and table 11. The numerical noise tolerance is + 3 db (A). Rounding interval is 1

Table 10

| Power kW | Synchro-speed r/min |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 3000 | 1500 | 1000 | 750 | 600 | 500 |  |  | 429 |  | 375 |
|  | Sound power level dB（A） |  |  |  |  |  |  |  |  |  |  |
| 0.12 | — | 52 | — | — | — |  |  |  |  |  |  |
| 0.18 | 61 |  | 52 | 52 |  |  |  |  |  |  |  |
| 0.25 |  | 55 |  |  |  |  |  |  |  |  |  |
| 0.37 | 64 |  | 54 | 56 |  |  |  |  |  |  |  |
| 0.55 |  | 58 |  |  |  |  |  |  |  |  |  |
| 0.75 | 67 |  | 57 | 59 |  |  |  |  |  |  |  |
| 1.1 |  | 61 |  |  |  |  |  |  |  |  |  |
| 1.5 | 72 |  | 61 | 61 |  |  |  |  |  |  |  |
| 2.2 |  | 64 | 65 | 64 |  |  |  |  |  |  |  |
| 3 | 76 |  | 69 |  |  |  |  |  |  |  |  |
| 4 | 77 | 65 |  | 68 |  |  |  |  |  |  |  |
| 5.5 | 80 | 71 |  |  |  |  |  |  |  |  |  |
| 7.5 |  |  | 73 |  |  |  |  |  |  |  |  |
| 11 | 86 | 75 |  | 70 |  |  |  |  |  |  |  |
| 15 |  |  |  | 73 |  |  |  |  |  |  |  |
| 18.5 |  | 76 | 76 |  |  |  |  |  |  |  |  |
| 22 | 88 |  |  |  |  |  |  |  |  |  |  |
| 30 | 90 | 79 |  | 75 |  |  |  |  |  | 90 |  |
| 37 |  | 81 | 78 | 76 |  |  | 90 | 90 |  |  |  |
| 45 | 92 |  | 80 |  | 82 |  |  |  |  |  |  |
| 55 | 93 | 83 |  | 82 |  |  |  |  |  | — |  |
| 75 | 94 | 86 | 85 |  |  |  |  |  |  |  |  |
| 90 |  |  |  |  |  |  |  |  |  |  |  |
| 110 | 96 | 93 |  |  | 90 |  |  | — |  |  |  |
| 132 |  |  |  | 90 |  |  |  |  |  |  |  |
| 160 | 98 | 94 | 92 |  |  |  | — |  |  |  |  |
| （185） |  |  |  |  |  |  |  |  |  |  |  |
| 200 |  |  |  |  | — |  |  |  |  |  |  |
| （220） | 100 | 95 |  |  |  |  |  |  |  |  |  |
| 250 |  |  |  | — |  |  |  |  |  |  |  |
| （280） |  |  |  |  |  |  |  |  |  |  |  |
| 315 |  |  | — |  |  |  |  |  |  |  |  |
| 355 | 103 |  |  |  |  |  |  |  |  |  |  |

Table 11

| Center height Hmm | Synchro-speed r/min |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 3000 | 1500 | 1000 | 750 | 600 | 500 | 429 | 375 |  |
|  | Sound power level dB（A） |  |  |  |  |  |  |  |  |
| 90≤H≤160 | 2 | 5 | 7 | 8 | － | － | － |  | － |
| 180≤H≤200 |  | 4 | 6 | 7 |  |  |  |  |  |
| 225≤H≤280 |  | 3 |  |  |  |  |  |  |  |
| H=315 |  |  | 5 | 5 | 7 | 7 | 7 |  | 7 |
| H≥355 |  | 2 | 4 | 4 | 6 | 6 | 6 |  | 6 |

- Outline and installation dimensions

Refer to Fig.4, Fig.5, Fig.6, Fig.7, and Fig.8 for the motor outline and installation dimensions.

- Installation and operation

Attention!

During motor installation, it is not allowed to hit the motor by heavy objects, lest make frame deformation or damage the bearings and other components.

Temporary alignment problems happen for every motor and driven equipment during installation process, it is likely to cause deformation of motor parts during the transportation. Therefore, it is necessary to do alignment work after installation.

1.The following checkup should be made before installation. And the motor cannot be put into use unless it had been certificated.

1)  There are explosion-proof marking and explosion-proof certificate serial number. A safety sign of mining product is a must for coal mine motor.

2)  The protection grade and group should reach the application requirements of the explosive gas atmosphere.

3)  All the tightening bolts must be fastened, the spring gaskets exist and the flameproof joint surfaces are matched perfectly.

4)  All the flameproof parts are out of crackles and faults that mitigate the flameproof effect. (The intact motor components may exempt from inspection).

5)  After long-distance transportation or long-term unused, insulation resistance of the motor winding to the motor shell should be measured by 500 v or 1000 v megger(motor rated voltage is greater than 500 v). Hot insulation resistance of the new motor shall not be less than R = U/P / 100 (1000 +) Ω (M)), cold insulation resistance shall not be lower than 5 m Ω (recommended the minimum value, actual use value is greater than the minimum), otherwise it should be dried until the insulation resistance value higher than the specified value. The drying methods are hot air blowing, incandescent lamp or heater and so on. Anyway, the motor winding temperature must be rise in the process of drying, but not more than the specified temperature limit of the winding insulation class.

6)  The motor acceptance testing can be ignored because pressure test has been done  before delivery. Please contact the manufacturer if necessary.

7)  For long-term unused motor, the rolling bearing grease should be checked before installation. If the original grease has been bad, dry or dirty, it should be replaced by the new grease. Bearings should be cleaned by cleaner or pure clean gasoline before the replacement. New grease weight W of each bearing can be calculated as followed:

W=D·B / K     g

D—Bearing outside diameter  mm

B—Bearing width  mm

K= Coefficient can be selected from 100 to 200, the minimum value is selected for the worse work condition

Non-stop oiling or discharge device was equiped for the motor ( only apply to frame size 160 and above. Grease are not necessary for frame size 160 and below motor, they are sealed bearing). According to the operation condition or schedule time in refueling instruction nameplate, you can infuse the oil through the oil cup into the motor by oil gun. While filling, you should rotate the axis and make a new uniform distribution on the bearing grease. The bearing temperature will rise after adding the grease, but it will return to normal level while the motor run for a period of time, and excess grease will flung out of the bearing.

8)  Before driving, the motor should be idle for a period of time, and then check and measure whether there are abnormal noise, vibration, local overheating or abnormal rotation direction. For the motors that can rotate positively and negatively, the two motor power supply terminals can be exchanged if the rotation direction turned inside out;  For the motors that can only rotate positively or negatively, the motor rotation direction should be confirmed before the join operation of equipments. Rotation requirements of direction signs and the connecting device should be consistent, otherwise the connecting device will be damaged. If turned inside out, please contact the manufacturer. (If the alphabetical order(U, V, W or U1, V1, W1) of the motor terminal box terminals and voltage phase sequence (A, B, C) are in the same direction, such as U and A, B and V, W and C connection, the motor direction of rotation is clockwise (from the motor shaft extension end point). If you change any two phase connection (such as U and C, V and B, W and A connection), the motor direction of rotation will be changed too.)

9)  The connection of motor and motor base

a) Install the motor base on the foundation or other support, and add shims to find level. In order to make sure the base surface in a horizontal plane after the anchor bolt is tightened, you should check in two 90 ° directions with a laser or gradienter. Put the motor on the base, then install and screw down the base bolt or nut. Never tighten the base bolt or nut except that you have done the alignment.

b) During installation, if the motor footing hole not match with the base or anchor bolt, and it is really necessary to ream hole, you should conduct lineation firstly, and bore hole by the method of gold processing. The wind electric welding cutting can only be used for steel base if no suitable condition. Pls cut by rules, and reduce the cutting deformation caused by cutting as much as possible.

2. The insulation resistance between the stator windings and the ground should be no less than 0.38MΩ(at 380V rated voltage) or 0.66 MΩ(at 660V rated voltage), 1.14 MΩ(at 1140V rated voltage).( The insulation resistance should be no less than following formula R=U/(1000+100/P) MΩ.

3. With the coupling connection, both the shaft lines of the motor and the driven equipment should be aligned to prevent the damage to the bearings and the breakup of the shafts.(Belt drive and converter connection are forbidden) . (The belt drive and frequency converter connection are not allowed)

Centered

Between the motor and driven equipment, its transmission shaft must be accurately centered. Incorrect centering can cause vibration, bearing overload and axial stress, flexible coupling can offset tiny wrong centering. The basic principle of centering is: no more than 5 pieces of baseboard spacer should be placed under the bottom of the motor. Spacer group made up of many shims can "soften" the bottom baseboard, leading to vibration or frame deformation (bottom baseboard of the motor is not in the same plane).

After positioning unit properly obtain axial movement, separate the coupling and install an indicator at the rigid coupling end of it, and the probe was installed on the cylindrical surface which is at the other end of the coupling, as shown in figure 9. At the same time, rotate both ends of the rotating shaft, read the data on the top, bottom and sides of the coupling. Read the difference between the top and the bottom data, the difference of both sides’ data, thus make them as the basis of the centering. The maximum deviation does not allowed to be more than 0.05 mm for the flexible coupling, and 0.025 mm for the rigid coupling. Also, even when the unit connected, angle and vertical centering should be detected, and the indicator reading can't be more than 0.05 mm, as shown in figure 10 and figure 11.

Figure 9 parallel unalignment schematic diagram

Figure 10 Angle unalignment schematic diagram

Figure 11 vertical unalignment diagram

4. Power supplies

1) Select proper cables according to the nominal current and working conditions of the motor. For the cables led into the terminal box, their diameters should match the diameter of the seal ring (The rubber concentric circles may be stripped off to achieve proper diameter). Confirm that there is no gap between the seal ring and the cable, and between the seal ring and the connection box after the cover of the connection box is pressed tightly. Otherwise it will not function as explosion-proof.

2) When connecting the wires, the core wires of inlet cables and inner grounding should be inserted in between the two washers and be fastened. Note that the core wires should not extrude from the washers. (The aluminum cables should be led by copper-aluminum joint lugs). Ensure the good contact and reliable connection.

3) For the terminal box with 6 terminals, the connection can be changed by lugs so as to the star-delta starting can be achieved by changing the voltage. If the connection box has two inlets and only one of them is applicable, the plugging rod of the idling inlet should not be removed in case of forming an opening that impairs the explosion-proof effect.

4) Heater can only be used when the motor stopped work, and vice versa.

| Phase order | A | B | C |
| --- | --- | --- | --- |
| Head | ## U1 | V1 | W1 |
| End | U2 | ## V2 | W2 |

PS: When the power leads and heated wire are elicited in the same terminal box, phase sequence W2, U2, V2 connect with the main power supply, phase sequence U1, V1 connect with heated power cord, and cancel the connection strap; When the power leads and PTC thermistor are elicited in the same terminal box, phase sequence W2, U2, V2 connect with the main power supply, phase sequence U1, V1 and V1, W1 respectively connect with PTC thermistor signal lines(one for use, V1 for sharing side), and cancel the connection strap.

5) The inner grounding bolts should be earthed perfectly.

5. Trial run

Warning!

In order to prevent accidental exposure to the charged body or rotating part, before directly contact with the equipment of charged and the working parts of the motor in the process of debugging, usage, wiring, parts replacement, all the equipment must be blackouts, disconnected and isolated to avoid personal and equipment damage.

1) The phase sequence U, V, W of the motor should correspond to the phase sequence A, B, C of the input power supply respectively, then the motor can run clockwise when viewed from the shaft extension end.

2) Unless the deviation for power supply’s frequency (at rated voltage) and rated frequency is less than 1%, or the deviation for voltage (at rated frequency) and rated voltage less than 5%, the motor cannot give off the rated power continuously. For the continuous duty type, the overload must be forbidden.

6. The maximum surface temperature of the motor housing (when measured with the thermometer) should not exceed 130℃ even if it works under the most severe pemissible conditions.

7. When the motor is running, it shall not exceed the rating value given on the nameplate, also not contrary to the descriptions in instruction manual. All the motors have been tested before delivery, and are qualified products. It will cause abnormal stress and strain if operate beyond the rated value, even cause damage to the motor and personal danger if you ignore this warning.

- Maintenance

During the design process, it has been considered and guaranteed that the motor will be in safe operation for years and need maintenance as less as possible. But it does not mean that the motor can work smoothly even if you ignore or delay maintenance.

  - The motor should be cleaned and examined regularly. Dust should not accumulate on the housing and the motor shouldn’t be cleaned with water.

  - Electrical and mechanical malfunctions are two factors which request for the normal maintenance. The first phenomenon of the electrical failure is usually low insulation resistance. Mechanical failure usually shows bearing abnormal noise or overheating.

  - Usually, the following factors will cause low insulation resistance: (Please refer to above measuring method for insulation resistance)

a. Mechanical damage of the insulation

b.Insulation thermal metamorphism

c. Too wet

d. Dirty coil (with oil, dirt, grease, etc.)

Dirty coil can be clean up and wet coil can be dried. But a and b can only be repair by the manufacturer or professional maintanance factory. If the motor was affected with damp, it must be dried by hot air blowing, incandescent lamp, heater, drying furnace or short circuit current.

In the process of drying, motor winding temperature will rise gradually, generally not more than 120 ºC. If dry with the short circuit current method, the motor is in short circuit condition, the input current should appropriately be 0.6 ~ 0.8 times of the rated current value. It is unfavorable to dry the motor by direct current drying method if it was seriously affected with damp, lest cause electrolytic phenomenon.

  - Motor bearing life can be extended if given proper maintenance, accurate centering and good lubrication performance. Incorrect centering can cause bearing overload, and generate excessive vibration and thrust. In order to ensure that the motor can be directly put into operation under normal circumstances, rolling bearing has been infused with lubricating grease before delivery. The motor grease should be checked regularly after the motor put into operation.

  - The replaced bearing may be the product of different manufacturer, but must be the same as the original used on motor bearings. As to the model, pls refer to the below table or the original motor bearing. Pay attention to the bearing's precision grade when you choose new bearing.

  - Pay special attention to a common mistake, that is too much lubrication of bearings. When there is extra grease and not discharged by oil discharge unit, the excess grease will be everywhere, and may enters the coil through the bearing inner cover, or may increase the bearing temperature. Excessive lubrication caused more harm consequences than that of insufficient lubrication.

  - The bearing greases with different specifications are not allowed to mix together. The mixture can make the grease soft, and will lead to poor performance of grease lubrication, thereby reduce the service life of the grease, or will reduce the service life of the bearing.

  - When the motor is running, the bearing is allowed to run at temperature - 15 ~ 95 ºC (thermometer method). As to frame size 160 and below motor, they have sealed bearing and do not need grease. For frame size 160 and above motor, it should be checked at least once every 2500 hours (about half a year). If the original grease has been bad, it should be replaced by the new one. The bearing should be cleaned by gasoline before the replacement.  2 # lithium base grease can be used for ?, and the extreme pressure of high temperature compound lithium base grease7019-1 (2) can be used for 315 ~ 355. The amount of refueling for the 2 pole motor is 1/2 bearing chamber volume, and 2/3 for those 4 pole motor. The bearing types are shown in table 10.

Table 10

| ### Base number | Extension end of shaft |  | Non-extension end of shaft |  |  |
| --- | --- | --- | --- | --- | --- |
|  | 2 Poles | Above 4 Poles | 2 Poles |  | Above 4 Poles |
| H63 | 6201-2RZ |  |  |  |  |
| H71 | 6202-2RZ |  |  |  |  |
| H80 | 6204-2RZ |  |  |  |  |
| H90 | 6205-2RZ |  |  |  |  |
| H100 | 6206-2RZ |  |  |  |  |
| H112 | 6306-2RZ |  |  |  |  |
| H132 | 6308-2RZ |  |  |  |  |
| H160 | 6309-2RZ |  |  |  |  |
| H180 | 6311 C3 |  |  |  |  |
| H200 | 6312 C3 |  |  |  |  |
| H225 | 6312 C3 | 6313 C3 | 6312 C3 |  |  |
| H250 | 6313 C3 | 6314 C3 | 6313 C3 |  |  |
| H280 | 6314 C3 | 6317 C3 | 6314 C3 |  |  |
| H315 | 6317 C3 | NU319 C3 | 6317 C3 | 6319 C3 |  |
| H355 | 6218 C3 | NU320 C3 or 6320C3 | NU218 C3 | 6320 C3 |  |

  - When you disassemble the motor, pls pay attention to protect flame-proof surface (refer to figure 1, motor structure). flame-proof surface shall be coated with rust-proof oil 204-1 when you assemble the motor, and seams surface shall be coated with liquid sealant 704. If there is a slight corrosion phenomenon, you can wipe the rust layer by the available gasoline rag, and then coat it with rust-proof oil 204-1. When you assemble the motor, you must ensure that the cavity in the motor be dry, clean and no foreign body, and make sure that there is no dirt and sundries in bearing and lubrication chamber, and then install oil plug.

  - Please follow the information on the nameplate of the motor base and correctly use the motor, the information is also essential to your order and motor maintanance.

  - Overload operation can lead to overheating and reduce the insulation life. If the winding temperature exceed 10℃ out of its maximum limit temperature of insulation class, the insulation life will be reduced by half. High temperature also can destroy insulativity. So pls carefully control the temperature and avoid hot spot.

- Matters need attention

  - The motor should be kept in dry and ventilated storage places.

  - The motor shouldn’t be placed upside down during storage and transportation.

  - It is not allowed to lift the motor by the shaft extension when the motor is hoisting, in case that the  shaft extension become bending deformation. The motor is equipped with the lifting device for transportation. The motor should be transported and installed by experienced workers. Lifting rings on the motor base are dedicated to hook and line transportation. Pay attention to the weight of the motor before lifting. The weight has been marked on the outline installation size chart and motor nameplate. You can only use the lifting lug on the motor base. Pls tighten the lifting lug and don't yank or suddenly move the motor.

  - The inlet cable cores should be fastened and pressed with the connection press plate to avoid the cable movement. Otherwise, short circuit will occur and consequently, will cause discharge explosion.

  - The external grounding bolts should be grounded reliably.

  - The motors are forbidden to work under overload conditions or they might burn down because of overheat.

  - When the explosion-proof components on the motor housing are damaged, they should be replaced immediately. Or the motors will lose their explosion-proof capacity and hence impair the safe production.

  - It is strictly prohibited to open the cover when it was charged.

  - Motor fastener must be replaced by the products with the same specifications.

- Frequent failure of motor and the troubleshooting

  - The frequent failure of motor and the troubleshooting is as follows:

| Failures | Root reason of failures | Troubleshooting |
| --- | --- | --- |
| 1. Motor can not be started | 1) No power | 1) Check the switch, fusant, contact point and he joint of the outgoing line of motor. |
|  | 2) Open circuit of winding or the winding breaks. | 2) Heating the open circuit/broken section to the temperature required by the insulation class so as to make the lacquer softened, and then pick up the broken line, use the one with the same specification to re-solder the broken section, and then wrap it with the insulation materials, then coats the lacquer and dry it. |
|  | 3) Short circuit of winding grounding or phase | 3) The solution is as the above, but one more issue that needs to do is to make the grounding or cushion of the broken section insulated, and then coats it by lacquer, then dry it. |
|  | 4) Wrong connections of winding | 4) Check the connection diagram. |
|  | 5) The fusant melted. | 5) Find out the reason to solve the failure, and provide the new fusant as per the specification of motor. |
|  | 6) Wong connections of control equipment | 6) Check and correct the connections. |
| 2. The fusant melted when the motor switches on the power supply | 1) Single phase startup | 1) Check the power supply cables, outgoing lines of motor, fuse, each contact point of switch, find the broken cables and then repair. |
|  | 2) Motor is overloaded or shocked. | 2) Adjust the loading to a rated value, and then solve the possible failure. |
|  | 3) The cross section of fusant is too less. | 3) Change another fuse with a big content. |
|  | 4) The connections between the power supply and motor is broken. | 4) Check the short circuit (breaking point), and the repair. |
| 3. The motor fails to start after being switched on, but only with a buzz sound | 1) The motor is overloaded or shocked. | 1) Check the equipment to solve the failures. |
|  | 2) Insufficient power is supplied. | 2) Replace the fusant of the fuse, tightening the screws of the wire holder; checking the broken sections of power line or the wrong connection, and the repair |
|  | 3) Low voltage | 3) If the power supply is insufficient, the power supply department should be contacted; if the voltage of power line reduces too much, a thick cable should be used. |
|  | 4) Lubricating grease is too hard or the assembly is too tight. | 4) Choosing the appropriate lubricating grease to improve the assembly quality. |
| 4. The enclosure of motor produces electricity | 1) The power line and the grounding line is connected wrongly. | 1) Correct the error. |
|  | 2) The winding of motor dampens, the insulation is aged seriously. | 2) Drying the motor, replace the aged insulation. |
|  | The outgoing line and the terminal box is grounded. | 3) Wrap or replace the insulation of outgoing line, repair the terminal box. |

  - The frequent failures and troubleshooting of motor is as follows:

| Failure | Reasons | Troubleshooting |
| --- | --- | --- |
| 1. Motor vibrates | 1) Bearing is worn, gap is wrong. | 1) Check the gap between bearing. |
|  | 2) The air gap is uneven. | 2) Adjust the air gap and make it meet the requirements. |
|  | 3) The rotor is unbalanced. | 3) Check the reasons, clean it, and tighten all bolts, then make it balanced. |
|  | 4) The hardness of enclosure is insufficient. | 4) Find the insufficient point, and then reinforce it to increase the rigidness of enclosure. |
|  | 5) The strength of foundation is insufficient, the installation is not leveled. | 5) Reinforcing the foundation, make the grounding of motor flat, and then tighten it. |
|  | 6) The fan is not balanced. | 6) Repair fan, correct the geometry or correct it to balance. |
|  | 7) The shaft is bended. | 7) Correct the shaft. |
|  | 8) Metal core of rotor is deformed or loosened. | 8) Correct the metal core, and then relocate the metal core. |
|  | 9) Grounding bolt of motor is loosened. | 9) Tightening the grounding bolts or replace the nonconforming grounding bolt. |
| 2. The heat of bearing is out of the allowable requirement | 1) The lubricating grease is too much or too less. | 1) Feeding correct lubricating grease as per the instruction. |
|  | 2) The oil is poor quality, impurities are contained. | 2) Check if there contains impurities, replace clean lubricating grease. |
|  | 3) The seal of oil is too tightened | 3) Replace or repair oil ring. |
|  | 4) The inner cover is of eccentricity, and contacts with the shaft. | 4) Repair the inner cover of bearing, make an appropriate gap between it and the shaft. |
|  | 5) The end cover at the both sides of motor or the bearing is located incorrectly. | 5) Place the end cover or bearing cover into the stop port by following the correct technology, and then tightening screws evenly. |
|  | 6) The bearing is defective, or worn or contains impurities and others. | 6) Replace damaged bearing, clean the bearing that contains impurities completely, and then replace the oil or grease. |
|  | 7) The motor and the driving mechanism is connected wrongly, or the driving belt is too tightened. | 7) Correct the central line between the motor and the driving mechanism, and adjust the tension of the driving belt. |
|  | 8) The inappropriate bearing is chosen, when it is overloaded, the load for rolling bearing is too much. | 8) Choose appropriate bearing type. |
|  | 9) The gap between bearing is too big or too less. | 9) Replace the bearing. |
|  | 10) The oil ring of sliding bearing turns stiffly. | 10) Repair oil ring, correct the size of oil ring and then make it balanced. |

- The delivery of goods and Three Guarantees service

1) Generally, the motor delivery is railway or highway transport. The motor has been inspected and packaged before delivery. It will be protected in storage and transportion stages.

2) when you receive the goods, pls check if there are damages to the motor during transportion.  You also have to check the motor before it was unloaded from the truck. If there is obvious rough handling, pls immediately put in a claim to shippers, and timely notify the jiangsu xianda explosion-proof co., ltd.

3) In accordance with the regulations of the instruction, and under the conditions of the proper use and storage of the motor, manufacturers guarantee that the motor can work well within 12 months from the operation date or 18 months from the shipment date. If the motor damage due to poor quality or not work properly in the specified period, manufacturers will repair or replace parts until the motor works well.

If the problems caused by other reasons and the motor can't work well, manufacturers can provide maintanance service, but will need confirmation and charge fees. If you encounter any problems in the motor operation, welcome to contact us as follows, and we will serve you wholeheartedly.

- Address

528#, Chunhui Road, Wuxi Huishan Economic Development Zone, Wuxi City, Jiangsu Province

Tel:  0510-83591888,83591777,83591666

Fax: 0510-83761666

P.C: 214177

Http://www.xianda.com

E-mail: xianda@xianda.com